## RFP Conditions
Supplier/ Manufactures name:
Address :
Tick the check box in column C if items in column B are inclusive/complied/submitted. Give any comments in column D.
The scope includes, |  | Comments if any
1 | Batteries- Battery module, Battery enclosure / unit
2 | Inverters
3 | EMS
4 | Power Park Controller
5 | Stand-by / auxiliary / emergency power requirements
6 | Environmental impact mitigatory measures
7 | Step up Transformer
8 | Auxiliary Transformer
9 | Switch gear & protection schemes
10 | SCADA facilities up to the Termination Point
11 | Energy Meters
12 | Power conditioning system
13 | Grid Code compliance monitoring system
14 | All other appurtenant equipment i.e., Cooling Systems, etc
15 | If any other please specify.
The BESS and its auxilliaries can comply with the following,
1 | The BESS will be available for 400 full equivalent cycles per year. (at least 20 cycles per month)
2 | Will guarantee a minimum system availability of 97% on monthly basis.
3 | Will demonstrate, on annual basis, 100% of the minimum Dispatchable capacity of the BESS. Taking into consideration capacity degradation, the minimum dispatchable energy to be made available by the Project Company at the end of a given year shall be as follows:
4 | Will guarantee a minimum AC to AC roundtrip efficiency (RtE) minimum 85% for the system on monthly basis.
5 | Type & ratings of major equipment, MV & LV switch gear, etc.(the maximum fault levels for each grid substation are given below) Can comply with specified maximum fault levels.
6 | Protection scheme proposed to be provided for the bus-bars, transformers, inverters and other applicable switchgears, including fire protection to comply with the provisions of Grid Connection Code and “CEB Guide for Grid Interconnection of Embedded Generators” and as amended. Protection schemes may have interfacing with power system equipment and these protective schemes shall be subjected to the concurrence of NSO.
7 | Equipment offered shall be new and unused. All equipment and plant design must conform to NSO regulations applied to any power plant connected to Sri Lankan power system as stipulated in the Annex A, B and C, Volume I of the RFP.
8 | The meters/recorders will meter, record, and transmit the data on the power/energy flow to the NSO system.
9 | Will provide Industrial grade, independent SCADA gateway for integration with National System Control Center.
10 | SCADA gateways will comply with the IEC 60870-5-104 for Master station standards.
11 | Equipment and port redundancy will be available for the SCADA gateway. In case of a main one failure, standby unit shall be able to switch to main operation with NSCC.
12 | Will provide a reliable technical solution to integrate the data feeds from dual redundant sources to the gateways, ensuring the seamless SCADA reporting with precise time stamps.
13 | All the signals related to BESS Facility as per typical signal lists attached as Annex D of Volume I of RFP shall be configured in the Gateway as per the IEC 60870 – 5 – 104 protocol and made available to SCC by Project Company via the NTNSP communication equipment at the relevant Grid Substation before the commissioning. Gateway configuration parameters are given in Annex D of Volume I of RFP. The communication interfaces will be configured as in Annex D of Volume I of RFP. Finalized Signal List will be submitted at least 02 weeks prior to the commissioning.
Following will also be included in the scope,
14 | Fiber Optic Cable from BESS to Grid - Two (02) nos. separate fiber optic cables (for redundancy) will be drawn from BESS to the Grid Substation. The fiber cable will contain 8 nos. of single mode fiber cores suitable for transmission of 1310 nm and 1550nm optical wavelengths and they will be in conformity with ITU-T recommendations G.652.D.
15 | A suitable distribution frame/patch panels with single mode pig tail (FC) terminations will be installed at two ends of FO cables to terminate 48 Nos. of cores. Suitable all dielectric ruggedized optical fiber approach cables will be used from the outside switchyard joint box to the indoor patch panel of Grid Substation.
16 | A suitable DC powered firewall with redundant power supply units will be supplied, installed and commissioned (to suit the NSO/NSCC recommended security rules/policies) at the Grid Substation. And from this firewall there will be 02 Nos. of parallel 1 Gbps optical Ethernet links on the two redundant optical fiber cables, commissioned up to an appropriate firewall/network switch installed at the BESS end. The firewall at Grid Substation may require NAT (network Address translation) facility for masking the internal subnets.
17 | At the grid substation from this new firewall there will be 02 Nos. of Electrical 1000Base T type parallel links (trunks) to the existing optical multiplexer to interface SCADA and Voice over IP facilities tagged with IEEE 802.1Q VLANs.
18 | An IP desktop phone will be made available at BESS to provide operational voice communication with NSCC.
Documents to be submitted
1 | Filled RFP Volume II Section 6- Technical Specification table (Attached form to be fiiled)
2 | BESS Modules to be installed should comply with the relevant International Standard as per Section 6 of Volume II of RFP (IEC 62619, IEC 62620, IEC 62902, IEC 62485-5, IEC 63056, IEC 62933-1, IEC 62933-2-1, IEC 62933-5-2, UL 9540, UL 9540A, UL 1973, UN 38.3, etc or latest available equivalent Standards) Document evidence for compliance.
3 | Inverters and Power Conditioning Systems shall comply with the latest editions of the following standards: IEEE 1547-2018 (Standard for Interconnection and Interoperability of Distributed Energy Resources), IEEE 2800-2022 (Standard for Interconnection and Interoperability of Inverter-Based Resources Interconnecting with Associated Transmission Electric Power Systems), UL 1741-SB (Inverters, Converters, Controllers and Interconnection System Equipment, Supplement B for Grid Support Utility Interactive Inverters), IEC 62477-1, IEC 62109-1/2, IEC TS 62786-3 (stationary battery energy storage connected to the grid), and the relevant requirements of the Sri Lanka Grid Connection Code dated 22 July 2024 Document evidence for compliance.
4 | Technical document of Batteries
5 | Technical document of power convertors
6 | Technical document of transformers
7 | Details of Protection schemes
8 | Details of SCADA and Telecommunication system
9 | Land requirement - Submit the detailed typical BESS Layout document to understand the land requirement with dimensions.
10 | A documents including required number of battery modules, inverters, and associated control systems for the project
11 | Relevant literature, brochures, or technical documents describing the manufacturer’s business, facilities, and organizational capabilities.
12 | Documents of track record, to prove the technology
13 | Filled form of Experience record of the proposed battery energy storage equipment/ PCs manufacturer/ supplier (Attached form to be filled)
14 | Project Milestone schedule – should achieve COD within 6 months (order placement, deleivery, erection, commisioning, ect)
15 | Operation and Maintenace manual and plan for O&M activities
16 | Details of auxiliary Power consumption during charging, discharging and idle
17 | Disposing process at the end of the period-recommendation
18 | Civil foundation drawings and other civil work related requirements
19 | Logistics requirements, Road transport and shipping conditions
20 | Single line diagram
21 | Submit initial non-site-specific simulation models of the BESS in both PSS®E and PSCAD™/EMTDC™ formats along with the tender for evaluation OR provide test results with the tender, demonstrating the BESS response in terms of voltage (V), active power (P), and reactive power (Q) during deep and shallow faults, and for a +50-degree phase angle step change at the Point of Connection (POC), under Short Circuit Ratio (SCR) levels of 1, 3, 5, and 10, with an X/R ratio of 5
22 | Warranty details (Basic warranty certificates for each equipment) and if extended for 15 years
23 | Warranty details for each equipment with Long term services agreement
24 | Draft Long Term Services Agreement with commercial terms
25 | List of Spares
26 | Expression of Interest to supply
27 | Commercial offer for supply of each equipment with basic warranty
28 | Commercial offer for the extented warranty of equipment
29 | Commercial offer for LTSA
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if complied
Tick if complied
Tick if complied
Tick if complied
Tick if complied
Tick if complied
Tick if complied
Tick if Complied
Tick if Complied
Tick if Complied
Tick if Complied
Tick if Complied
Tick if Complied
Tick if Complied
Tick if Complied
Tick if inclusive and complied
Tick if inclusive and complied
Tick if inclusive and complied
Tick if inclusive and complied
Tick if inclusive and complied
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if submitted
Tick if inclusive
Tick if inclusive
Tick if inclusive
Tick if inclusive

## Functional Performances
Comment on the compliance infront of each requirement
A.02.04. | Temperature and Humidity | Comply/ Non Comply (Comment if any)
| 10 ºC to 40 ºC The SVS shall operate in a curtailed mode if the temperature falls outside of the operating range. The Project Company shall specify such degraded ratings in the proposal. | comply
| The design relative humidity shall be 95%, measured over a period of 24 hours. | comply
A.03. | Conditions for Connection of BESS
| Clause 3 of the Grid Connection Code should be complied | comply
A.05. | Technical Requirement
| BESS shall have grid-forming control capabilities, providing short-circuit capacity to the system. During steady-state and transient processes, the grid-forming converter shall instantly share unbalanced grid power, respond to voltage changes, and inject reactive power. | comply
A.05.01. | Grid Connection Code
| Comply with Grid Connection Code approved by Public Utilities Commission in Sri Lanka dated 22 July 2024. | comply
A.05.02. | Frequency variation capability
| (a) BESS shall be capable of delivering the declared active and reactive power outputs within the system Frequency variations, specified in this specification. Additionally, the PCS AC-side current of the BESS shall be capable of operating continuously at 110% of the rated current, sustain 120% of the rated current for ≥2 minutes, and preferably support short-term overloads of 150% rated current for 10 seconds. | comply
| (b) Active and reactive power capability (±10 MW/ ±3 MVAr) of the BESS must be available for frequency range between 47 Hz to 52 Hz for at least for time related clause in A.05.04. ( consider real and reactive power loss transformer when calculating the BESS rating at POC. ) | comply
| (d) The supplied active power shall be delivered to the network based on the nominated frequency droop settings and deadband settings. | comply
| (e) BESS shall be protected against frequency excursion outside the frequency range specified in clause in A.05.04. and able to disconnect from the system if the extreme frequency could risk to the BESS performance and reliability. | comply
A.05.03. | Frequency support capability (refer figure A.05.03 in next sheet)
| (a) The BESS must be capable of responding independently on a configurable droop curve in response to frequency deviations, without receiving external control signals from CEB. | comply
| (b) Droop setting shall be able to set between 1% to 9% as per the CEB discretion. If CEB did not disclose any Droop value, then it shall be set at 4%. | comply
| (c) During a sudden frequency drop BESS shall mimic an inertia response of a synchronous machine through its grid forming control system. This synthetic inertia response shall be configured by the NSO as part of the design of the Facility for the purpose of maintaining network stability. | comply
| (d)The maximum inertia time constant of the grid-forming electrochemical energy storage system shall be no less than 20 seconds, with an inertia response activation time ≤5 ms. The system shall allow flexible adjustment based on grid requirements. | comply
| (e) The response time for primary frequency regulation shall be <0.2 s, with active power adjustment deviation ≤2%. | comply
| (f) No frequency regulation limit shall be set in principle, but if necessary, the limit shall be ≥20% Pn | comply
comply
A.05.04. | Frequency withstand capability (refer figure A.05.04 in next sheet)
| (a) BESS shall be capable of staying connected to the Transmission System and remain continuously operable within the System Frequency range 47 Hz to 52 Hz. | comply
| (b) BESS must remain connected and fully operational for under frequency variations between 47 Hz to 50 Hz for duration as shown in the following table and figure. Under frequency variation window shall extend to 45 Hz to 50 Hz if equipment has the capability to do so. | comply
| (c) BESS must remain connected and fully operational for over frequency variations between 50 Hz to 52 Hz for duration as shown in the following table and figure. Over frequency variation window shall extend to 50 Hz to 55 Hz if equipment has the capability to do so. | comply
| (d) Frequency ride through settings shall be configurable in at least four bands between 45 Hz – 55 Hz covering above requirement. If default band range capability of equipment exceeds this requirement, the default capability must be maintained and accessible to CEB without restriction. | comply
| (e) BESS shall change its power level up to its maximum rating according to the droop setting and frequency deviation in the system. | comply
A.05.05. | Rate of change of frequency
| (a) At a minimum, the BESS shall be able to remain synchronised to the system during rate of change of system frequency of up to and including 4.0 Hz per second measured at a rolling average over 250 milliseconds and 2.5 Hz per second measured at a rolling average over 500 milliseconds. | comply
| (b) Rate of change of frequency withstand capability mentioned in the A.05.05 (a) does not mean that equipment manufacturer or BESS developer intentionally set the BESS’ RoCoF protection to activate when RoCoF limit exceeds above limits in A.05.05. (a) unless violation is a risk to the device functionality or reliability. If any RoCoF protection of the BESS should be disabled unless it is essential to device stability and protection. | comply
A.05.06. | Voltage variation capability
| (a) The BESS shall be capable of delivering the declared active and reactive power outputs within the voltage variations of ±10% of the rated voltage at POC | comply
| (b) The BESS shall be capable of delivering the declared rated current during under voltage condition and over voltage conditions as mentioned in section A.05.08. | comply
A.05.07. | Voltage support capability
| (a) The BESS must be capable of responding on a configurable droop curve (1 – 6%) to either local voltage deviations or at POC, without receiving external control signals from CEB. | comply
| (c) The grid-forming energy storage system shall have automatic voltage regulation (AVR) functionality and the system’s 5% voltage step response time shall be <50 ms, with overshoot ≤30% of the voltage step magnitude. | comply
A.05.08. | Voltage withstand and fault ride through capability (refer figure A.05.08 in next sheet)
| (a) Under voltage variations, the BESS must remain connected and fully operational for duration as shown in the following table and corresponding figure. | comply
| (b) Voltage ride through settings must be configurable in at least ten bands between 0 and 1.3p.u. | comply
A.05.09. | Response to disturbances following contingency events
| (a) BESS must remain in continuous uninterrupted operation for any disturbance caused by: i. a credible contingency event ii. a three-phase fault in a transmission system cleared by all relevant primary protection systems (250 millisecond) iii. a two phase to ground, phase to phase or phase to ground fault in a transmission system cleared in: a. the longest time expected to be taken for a relevant breaker fail protection system to clear the fault; or b. if a protection system referred to in subparagraph (a) is not installed, the greater of the time specified by CEB (or if none is specified, 550 milliseconds) and the longest time expected to be taken for all relevant primary protection systems to clear the fault; or iv. a three phase, two phase to ground, phase to phase or phase to ground fault in a distribution network cleared in: a. the longest time expected to be taken for the breaker fail protection system to clear the fault; or b. if a protection system specified by CEB, the greater of 1000 milliseconds and the longest time expected to be taken for all relevant primary protection systems to clear the fault, provided that the event is not one that would disconnect the production unit from the power system by removing network elements from service. | comply
| (b) BESS and each of its production units must remain in continuous uninterrupted operation for a series of up to 6 disturbances within any five minute period caused by any combination of the events described in paragraph (c) where: | comply
| i. up to four of the disturbances (two LLLG faults, one LL and one LG fault) cause the voltage at the connection point to drop below 50% of normal voltage ii. up to one disturbance is cleared by a breaker fail protection system or similar back-up protection system iii. up to one disturbance causes the voltage at the connection point to vary within the ranges under clause A.05.08. . iv. provided that none of the events would result in: a. the islanding of the generating system or integrated resource system or cause a material reduction in power transfer capability by removing network elements from service b. the cumulative time that voltage at the connection point is lower than 90% of normal voltage exceeding 1,800 milliseconds within any five-minute period c. the time integral, within any five-minute period, of the difference between 90% of normal voltage and the voltage at the connection point when the voltage at the connection point is lower than 90% of normal voltage exceeding 1 pu second. | comply
| (c) BESS shall provide Inertia support during a fault i. The BESS shall provide a synthetic inertia support in response to a fault that mimics an inertia response of a synchronous generator. The maximum inertia time constant of the grid-forming electrochemical energy storage system shall be no less than 20 seconds, with an inertia response activation time ≤5 ms. The system shall allow flexible adjustment based on grid requirements. ii. This synthetic inertia response shall be configured by the NSO as part of the design of the Facility for the purpose of network stability, and subject to approval by NSO. | comply
A.05.10. | Reactive current injection and active power recovery during the fault (refer figure A.05.10 in next sheet)
| (a) Subject to any changed power system conditions or energy source availability beyond the BESS reasonable control, BESS respect of the types of faults described in subparagraphs clause A.05.09. must have BESS capable of supplying to or absorbing reactive current from the network: i. to assist the maintenance of power system voltages during the fault: a. BESS inverter shall inject reactive current during the fault (within their capability) based on the amount of remaining system voltage. Amount of reactive current during the contingency shall be equal to 2% for every 1% drop in voltage at the POC as a default value. Further, the BESS unit shall be capable of providing reactive current of x% per 1% drop in voltage at POC where x% shall be set between 1% to 6%. b. Additional reactive current injection during fault shall be in addition to the steady state reactive current given at that time by the BESS. c. during the disturbance and maintained until connection point voltage recovers to between 90% and 110% of normal voltage, or such other range agreed with the CEB; and ii. from 100 milliseconds after clearance of the fault, active power shall recover to at least 95% of the level existing just prior to the fault. | comply
| (b) CEB may request the contribution of positive, negative and zero sequence currents depending on the requirements of fault detection near the POC. | comply
| (c) Allowable activation delays are between 20ms - 40ms (in order for ac protection systems to detect faults without undue delays) and provide or absorb the required reactive current within 70 milliseconds | comply
A.05.11. | Quality of electricity generated (harmonic, flicker and voltage unbalance)
| (a) The BESS shall ensure that when connected to CEB network, it must not produce level of distortion or fluctuation of the supply voltage at the connection point: i. rapid voltage changes greater than 3% of the nominal voltage during the normal operation ii. harmonic voltage distortion greater than the emission limits allocated by the CEB in accordance to 3.17.2.5 of Grid Connection Code. a. harmonic analysis shall consider harmonic order 2 – 50 iii. voltage unbalance greater than the limits allocated by the CEB in accordance with IEC 60034-1. iv. voltage flicker greater than the limits allocated by CEB, i.e., Pst = 0.35 and Plt = 0.25. | comply
| (b) The design of the harmonic mitigation measures (including filters if required) shall be demonstrated through a harmonic analysis study. | comply
| (c) Measurement and evaluation of respective emissions shall be carried out in accordance with IEC 61000-3-6. Measurement and evaluation reports shall be prepared in accordance with IEC 61000-3-6 and IEC 61000-3-7. | comply
A.05.13. | Reactive power capability (refer figure A.05.13 in next sheet)
| (a) The BESS operating at: i. any level of active power; and ii. any voltage at the POC within the limits 0.9 and 1.1 per unit without a contingency event, | comply
| (c) must be capable of supplying and absorbing continuously at its POC (33 kV) an amount of reactive power of at least theamount equal to the product of the rated active power of the BESS and 0.3. | comply
| (d) must be capable to operate in any combination of exporting or importing active and reactive power, otherwise known asfour quadrant operation. | comply
| (e) If the BESS cannot meet the reactive power exchange requirements as outlined above, the Project Company shall expect to install additional equipment necessary to meet those requirements. | comply
A.05.14. | Voltage, reactive power and power factor control modes
| (a) The BESS shall be able to provide automatic control at the POC over the entire operating range of the BESS, without causing system instability. Control modes include: i. Voltage control ii. Voltage droop control iii. Reactive power control iv. Power factor control | comply
| (b) The BESS shall be capable of contributing to voltage or voltage droop control at the POC utilizing its capabilities, while respecting reactive power capability and reactive power exchange with the AC network, in accordance with the following control characteristics: i. Voltage set-point at the connection point shall be capable of being specified within the range (0.9 pu-1.1 pu), either continuously or in steps. ii. It shall be possible to operate voltage control with or without a dead band around the setpoint. The dead band shall be adjustable and agreed with CEB. iii. Voltage droop control mode shall include the capability to change reactive power output based on a combination of a modified voltage set-point and an additional instructed reactive power component (i.e. voltage-reactive power droop). The slope (i.e. voltage droop) shall be adjustable in the range (typically 2% -12%). | comply
| (c) The BESS shall be capable of operating at a designated reactive power value specified by the CEB as long as the same is within the reactive power capability of the BESS. | comply
| (d) The BESS shall be capable of controlling the power factor to a target at the POC, while respecting Reactive Power Capability and Reactive Power Exchange with the network. | comply
A.05.15. | Set point response
| (a) The BESS inverter must be able to respond independently to separate command set points from National System Control Centre (NSCC) for the following performance characteristics under normal operating conditions: i. MW ii. MVAr iii. power factor iv. voltage | comply
| (b) Set point response shall be by bias of the relevant droop curve and grid support functionality shall be maintained, within the active and reactive power capability limits of the BESS. | comply
| (c) The behavior of the relevant performance characteristic following receipt of a set point command at the Facility SCADA, subject to any pre-set ramp rate limitations, and limitations on the active and reactive power capability limits of the BESS, shall be as follows: i. Set point response must commence within 50 ms. ii. Commanded set point value must be achieved within 300 ms iii. Overshoot of the commanded set point value shall not exceed 10% of the value of the change in set point value. iv. Settling time, to within 1% of full-scale output for the relevant performance characteristic, must be achieved within 400 ms. v. BESS shall automatically notify NSCC when its state of charge moves outside the normal operating state of charge limits as described in Functional Specifications and reduce the active power set point to zero in a manner pre-agreed with CEB. | comply
A.05.16. | Priority to Active or Reactive power contribution
| (a) The BESS shall be capable of operating in the active or reactive power priority modes, as requested by CEB, while meeting continuous operating rating and short-term overload ratings. This includes utilizing the full rating (continuous and short-term overload) of the inverter current capability and operating in zero active power transfer. Taking into account the capabilities of the BESS, CEB may inform on case by case basis whether active power contribution or reactive power contribution has the priority during low or high voltage operation. | comply
| (b) If not specified active power control shall have the priority. | comply
A.05.17. | Control interaction with other generating devices
| (a) Control Interaction is a specific issue that can impact the coordinated operation of Power Electronic devices in a local area. Control systems of dynamic devices can interact in an undesirable manner resulting in unstable or poorly damped oscillations following system disturbances such as fault recovery. | comply
| (b) The BESS shall design the equipment to avoid such undesirable interactions, and the acceptable operation demonstrated through interconnection studies. | comply
| (c) The BESS shall be capable of contributing to the damping of power oscillations in theconnected AC Transmission system. The Project Company shall require to provide all required data control system models including parameters for of any small signal modulation controls such as power oscillation damping (POD) controls, or sub-synchronous oscillation damping controls. | comply
| (d) The grid-forming BESS shall have autonomous damping suppression functionality. When low-frequency oscillations (0.2 Hz–2.5 Hz) occur, the system shall suppress oscillations, with active power variation limited to 10%– 30% Pn. | comply
| (e) The BESS shall be capable to inject or absorb active phase jump power into the system immediately due to the change of phase angle in the event of disturbance or failure of the system | comply
| (f)Regarding the sub-synchronous torsional interaction (SSTI) damping control, the BESS shall be capable of contributing to electrical damping at torsional oscillation frequencies. The SSTI studies shall be undertaken by the NSO. The studies shall identify the conditions, if any, where SSTI exists and propose any necessary mitigation measures. | comply
| (g) The BESS shall be capable of finding stable operation points with a minimum change in active power flow and voltage level, during and after any planned or unplanned change in the BESS or AC Transmission System to which it is connected. | comply
| (h) The grid-forming BESS shall receive and respond to AGC (Automatic Generation Control) commands from the grid dispatch, with a regulation range of -100% to +100% Pn and steady-state active power deviation ≤2% Pn. It shall also receive and respond to AVC (Automatic Voltage Control) commands, with steady-state reactive power deviation ≤2% Pn. | comply
| (i) The BESS shall support both grid-following and grid-forming control modes, enabling online switching between the two. | comply
| (j) The grid-following mode shall operate stably under a minimum short-circuit ratio (SCR) of 1.2, while the grid-forming mode shall operate stably under a minimum SCR of 1.0. | comply
A.05.18. | Fault current
| (a) the contribution of the BESS to the fault current on the connecting network through its connection point must not exceed the contribution level that will ensure that the total fault current can be safely interrupted by the circuit breakers of the connecting network and safely carried by the connecting network for the duration of the applicable breaker fail protection system fault clearance times, as specified for the relevant connection point by the CEB | comply
| (b) BESS connected plant must be capable of withstanding fault current through the connection point up to the higher of: i. the level specified by CEB as per the clause A.04. ii. the highest level of current at the connection point that can be safely interrupted by the circuit breakers of the connecting network and safely carried by the connecting network for the duration of the applicable breaker fail protection system fault clearance times, as specified by the CEB. iii. circuit breaker provided to isolate a generating unit, generating system, bidirectional unit or integrated resource system from the network must be capable of breaking, without damage or restrike, the maximum fault currents that could reasonably be expected to flow through the circuit breaker for any fault in the network or in the generating unit, generating system, bidirectional unit or integrated resource system, as specified in the connection agreement. | comply
A.05.19. | Loss of communications
| (a) In the event of loss of communications, the set point response of the BESS shall automatically revert to a state as agreed with CEB during design of the Facility. | comply
| (b) Upon restoration of communications, the BESS plant shall not automatically restore operations but shall assess and issue ready status. Restart of operations shall only be commenced following instruction from CEB. | comply
A.05.20. | Safe shutdown
| (a) In the event network fault that leads to power system conditions outside the requirements of this specification, the BESS must automatically execute a safe and controlled shutdown. | comply
| (b) Upon restoration of standard operating conditions, the BESS plant shall not automatically restore operations but shall assess and issue ready status. Restart of operations shall only be commenced following instruction from CEB. | comply
| (c) Subject to the limits of the backup power supply of the Facility, communications and essential functions shall remain operational throughout a safe shutdown event. | comply
A.05.21. | Protection from power system disturbances
| (a) BESS to be automatically disconnected from the power system in response to abnormal conditions arising from the power system, the relevant protection system or control system must not disconnect the BESS for: i. conditions for which it must remain in continuous uninterrupted operation or ii. conditions it must withstand under the Grid Connection Code; and iii. a relevant system (as defined in paragraph (a)i connected to a transmission system must have facilities to automatically and rapidly reduce its generation: | comply
| (b) CEB may require the BESS to be automatically disconnected by a local or remote-control scheme whenever the part of the network to which it is connected has been disconnected from the national grid, forming an island that supplies load. | comply
| (c) Not withstanding clauses in Grid Connection Code or in this schedule, BESS may be automatically disconnected from the power system under any of the following conditions: a. in accordance with an ancillary services agreement between the BESS and CEB b. where a source of load that is not part of the BESS has the same connection point as the generating system and CEB agree that the disconnection would in effect be under-frequency load shedding c. where the generating system or integrated resource system is automatically disconnected under, Protection systems that impact on power system security or by an emergency frequency control scheme d. where the generating system or integrated resource system is automatically disconnected under Protection to trip plant for unstable operation; or e. in accordance with an agreement between the Project Company and CEB (including an agreement in relation to an emergency control scheme) to provide a service that CEB agrees is necessary to maintain or restore power system security in the event of a specified contingency event. | comply
A.05.22. | Data and information exchange between BESS and the System Control
| (a) Exchanged Information i. Regarding instrumentation for the operation, the BESS module shall be equipped with an automatic controller capable of receiving instructions from the CEB system control. This automatic controller shall be capable of operating the units of the BESS module in a coordinated way. | comply
| iii. The BESS controller shall be able to receive the following signals and commands from CEB based on communication with CEB. CEB shall specify the variable type and quality requirements of the supplied signals. a. Start-up command b. Active power order set-point c. Frequency sensitive mode settings d. Reactive power, voltage, or similar set-points e. Reactive power control mode f. Power oscillation damping (POD) control settings, if applicable g. Synthetic inertia, if applicable h. Normal and emergency blocking command i. Ramp blocking command j. Remedial Action Schemes status and settings k. Active power flow direction command, if applicable l. Fast active power reversal command, if applicable m. Redundancy reductions and auxiliary power single source status n. Other project-specific set-points and commands, as specified by CEB. | comply
| v. BESS EMS has the capability to record events where grid support services provided by the BESS and send the same data to NSO periodically. | comply
| (b)The developer of the BESS shall install Grid Code Compliance Monitoring system with following features at the point of Common coupling to ensure that the installed BESS operates in accordance with the Grid Code. The developer should integrate Grid Code Compliance Monitoring system to NSO's central monitoring infrastructure using standardized communication protocols. 3 and should provide comprehensive training for NSO personnel on system operation and data interpretation. Further, the developer shall establish a preventive maintenance program to ensure continuous system reliability. i. Real-time electrical parameter measurement: The device shall provides continuous monitoring of active power, reactive power, voltage, and frequency with high precision measurement capabilities. ii. Power quality monitoring: The device shall be capable of analyzing power quality including harmonic distortion measurement up to the 100th order, voltage unbalance detection, and flicker monitoring. iii. Fault ride-through monitoring: The device shall detect voltage sag events and validates compliance with low voltage ride-through (LVRT) requirements iv. Communication and control integration: The device shall support IEC 60870-5-104/101 protocols for seamless integration with NSO's SCADA systems v. Data storage and reporting: High-resolution data logging and automated compliance reporting capabilities. | comply
A.05.24. | Testing, monitoring and compliance review
| (a) Testing and compliance i. The BESS shall be designed and tested to meet the requirements of the CEB operational requirements, performance studies and any Interconnection Agreements. Sufficient monitoring shall be provided to CEB to determine that the BESS complies with those performance requirements. | comply
| (e) The BESS shall include any additional monitoring and recording required for the purpose of completing grid connection testing in the scope of supply. | comply

## Characteristic curves & tables
Power System Characteristics | A.05.03 Frequency Support Capability
A.05.04 Frequency Withstand Capability
A.05.08 Voltage withstand and fault ride through capability
A.05.10 Reactive Current injection and active power recovery during the fault
A.05.13 Reactive Power Capability